[image: image1]                                    TECHNICAL DATA SHEET


F/UTP 4Pairs cable-category5E- LSZH Sheath

P/N：G2302-024

	Content of the Data Sheet

	Sheath Printing
	TBD

	Customer No.
	
	Customer Reference
	
	[image: image2.wmf][image: image3.jpg]‘% ZHAOIONG





	Category
	F/UTP  CAT5E-4P-LSZH
	

	Reference Standard
	ISO/IEC11801、TIA-568-C.2 
	

	Conductor
	Material
	Solid-Bare Copper
	

	
	Nom.O.D.(mm)
	0. 510
	up
	+0.005
	

	
	
	
	down
	-0.005
	

	Insulation
	Material
	HDPE
	

	
	Diameter
	1.02±0.05 mm 
	

	Screening Material
	Mylar+ AL/Mylar
	

	Sheath
	Thickness
	0.55±0.05mm 
	Technical Performance (100m):
Frequency RL       ATT(20℃)       NEXT    PHASE DELAY

(MHz)     ≥dB 　    　≤dB    　　≥dB        ≤ns

1         20.0         —          65.3        570.00

4         23.0         4.1         56.3        552.00

8         24.5         5.8         51.8        546.73

10        25.0         6.5         50.3        545.38

16        25.0         8.2         47.2        543.00

20        25.0         9.3         45.8        542.05

25        24.3         10.4        44.3        541.20

31.25     23.6         11.7        42.9        540.44

62.5      21.5         17.0        38.4        538.55

100       20.1         22.0        35.3        537.60

Frequency   PSNEXT           ELFEXT          PSELFEXT

(MHz)        ≥dB             ≥dB             ≥dB

1            62.3             63.8              60.8

4            53.3             51.8              48.8

8            48.8             45.7              42.7 

10           47.3             43.8              40.8

16           44.4             39.7              36.7

20           42.8             37.8              34.8

25           41.3             35.8              32.8

31.25        39.9             33.9              30.9

62.5         35.4             27.9              24.9

100          32.3             23.8              20.8

	
	External O.D.
	6.3±0.4 mm 
	

	
	Surface
	Clean,Frap,Satiation
	

	
	Material
	LSZH(complies RoHS)
	

	
	Color
	TBD
	

	Surface Printing
	Letter height
	3.0±0.3mm
	

	
	Color
	Black
	

	
	Print error & Space
	≤±0.5%，1m
	

	Core Color
	1 White- Blue /Blue
	2 White-Orange /Orange
	

	
	3 White- Green /Green
	4 White- Brown /Brown
	

	Packing
	Wooden Tray & Carton
	

	Carton dimension
	According to the requires
	

	Packing length
	305±1.5m
	

	Rip-cord
	Yes
	Drain wire
	Yes
	

	Sheath  Physical

Properties
	Before Aging  Tensile Strength (Mpa)     ≥10.0
        Elongation(%)                  ≥125
	

	
	Aging Period( (℃×hrs)     100℃×24h×7d
	

	
	After Aging  Tensile Strength(Mpa)          ≥8.0
      Elongation(%)                       ≥100
	

	
	Cold bend(-20±2℃×4h)  8×Cable O.D.， No visible cracks
	

	Electrical

Characteristics

 (20℃)
	1.0-100.0MHz   Impedance(Ω)          100±15
	

	
	1.0-100.0MHz   Delay Skew (ns/100m) ≤45
	

	
	unbalanced-to-ground capacitance   （pf/100m)  max  330
	

	
	DC Resistance (Ω/100m) max                   9.5
	

	
	DC Conductor Resistance Unbalance (%)max      5.0
	

	Version
	A/01
	Date
	2017-08-25
	Revised By
	Caihanglie
	Audited By
	Nidonghua
	Approved By
	Nidonghua


	Number
	Revise Contents
	Revise Reasons
	Revised By
	Audited By
	Approved By
	Date

	A/01
	Specification Version 1
	
	Caihanglie
	Nidonghua
	Nidonghua
	2017-08-25

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	


� EMBED  \* MERGEFORMAT ���





White(blue)/blue








White-Orange/Orange








AL/Mylar








Mylar





Drain wire





White(green)/green








Rip-cord





White- Brown /Brown








Sheath













_1234567890.unknown

